## BDT
Battery Discharge Test (Autonomy Control)
Subcontractor: |  | Huawei | [5 empty] | Sub-office: |  |  | Mohandseen |  |  |  |  | Date: |  |  | 2024-01-28 |  |  | BDT Name
Site Name: |  | U_S_3938CA_BOLAKDAKROR27 | [5 empty] | Site Code: |  |  | 3938CA |  |  |  |  | Mobinil Area: |  |  | HGLI |  |  | U_S_3938CA_BOLAKDAKROR27_3938CA_BDT
Eng.Name: |  | Mohamed Ismail Mohamed Abdelaal | [5 empty] | Tech. Name: |  |  | NA |  |  |  |  | Time in: |  |  | Time In | 12:45:58
OMC Eng: |  | 56834 | [5 empty] | Tech. Name: |  |  | NA |  |  |  |  | Time Out: |  |  | Time Out | 12:55:33
[15 empty] | Rectifier Outside |  |  |  |  | Rectifier Inside
1 | Power Cabinet | [13 empty] | Clear photo for Rectifier |  |  |  |  | Clear photo for Rectifier
Power Cabinet # I
Power Source | [10 empty] | EC
Rectifier Type: | [10 empty] | Huawei
Number of operating modules installed | [10 empty] | 3
Number of faulty modules exists | [10 empty] | NA |  |  |  | Batteries Photo 1 |  |  |  |  | Batteries Photo 2
[15 empty] | Clear Photo for Batteries |  |  |  |  | Clear Photo for Batteries
Positive dc (0 vdc) / Ground | [10 empty] | 0
Negative dc (-48 vdc) / Ground | [10 empty] | 53.5
Positive dc (0 vdc) / Negative (-48 vdc) | [10 empty] | -53.5
2 | Rectifier Batteries | [13 empty] | Batteries C.Bs Photo |  |  |  |  | Batteries Rack / Cabinet | LVD disconnect set point
[15 empty] | Clear photo for batteries C.Bs at the rectifier |  |  |  |  | Clear Photo for Batteries | LVD disconnect set point
Battery brand | [10 empty] | Marathon
Number of batteries connected to the rectifier | [10 empty] | 8
Battery nominal voltage | [10 empty] | 12
Battery ampere hour | [10 empty] | 155
[15 empty] | Battery current |  |  |  |  | Rectifier Load current | PLVD set point
Number of strings | [10 empty] | 2 |  |  |  | Ibat before starting the test |  |  |  |  | Iload before Power disconnected | PLVD set point
Number of racks | [10 empty] | 1
Battery racks are connected to site ground | [10 empty] | Yes
Battery racks are fixed to shelter ground | [10 empty] | Yes
Number of intercell covers missing | [10 empty] | Yes |  |  |  | Charnging current limit |  |  |  |  | Battery diconnect / reconnect volt | Battery current after power reconnect
[15 empty] | Maximum charge current limit |  |  |  |  | Battery volt before diconnect the power | Ibat after 5 minutes of power reconnect
Separate distance exist between batteries (1 cm) | [10 empty] | Yes
Batteries are assembled according to specs | [10 empty] | Yes
All batteries are well tightened | [10 empty] | Yes
Clean batteries surface using a small moisten texture | [19 empty] | Battery volt before reconnect the power
All batteries are surface clean | [10 empty] | Yes
All battery poles are clean | [10 empty] | Yes
Number of Power Alarms since last 3 months | [10 empty] | 35
2.1 | Batteries discharge test
Rectifier |  |  | Rec Bus Bar |  | String # 1 |  | String # 2 |  | String # 3 |  | String # 4 |  | String # 5 |  | String # 6 |  | String # 7 |  | String # 8
Time: min (h) |  |  | V | A | V | A | V | A | V | A | V | A | V | A | V | A | V | A | V | A
Before disconnecting Rectifier |  |  | 53.5 | 70.7 | 53.5 | 0.1 | 53.5 | 0.2
10 Mins |  |  | 43.9 | 78.2 | 44 | 39.3 | 44 | 38.8
30 Mins
60 Mins
90 Mins
120 Mins
150 Mins
180 Mins
210 Mins
240 Mins
After Connecting power |  |  | 53.5 | 71.2
4. Site Equipment (Data)
[10 empty] | Site Type |  |  |  |  | Nodal
[10 empty] | Site Category |  |  |  |  | OD
[10 empty] | Mobinil Network |  |  |  |  | HGLI
[10 empty] | # of BSC |  |  |  |  | 0
[10 empty] | BSC Type |  |  |  |  | NA
[10 empty] | Type of 2G Cabinet |  |  |  |  | Huawei
3. Temp. Measured | [9 empty] | No. of 2G RF Modules Or MRFU |  |  |  |  | 6
Rectifier |  |  | Room Temp. ◦C | [6 empty] | Type of 3G Cabinet |  |  |  |  | Huawei
Time: min (h) | [9 empty] | No. of 3G RF Module Or RRU |  |  |  |  | 6
Before disconnecting Rectifier |  |  | 23 | [6 empty] | Type of 4G Cabinet |  |  |  |  | Huawei
10 Mins |  |  | 24 | [6 empty] | No. of 4G RF Module Or RRU |  |  |  |  | 2
30 Mins |  |  | 24.5 | [6 empty] | No. of SDH |  |  |  |  | 0
60 Mins |  |  | 25 | [6 empty] | No. of PDU |  |  |  |  | 0
90 Mins |  |  | 25.5 | [6 empty] | No. of ADM |  |  |  |  | 0
120 Mins | [9 empty] | Data for links |  |  |  |  | No. of link |  |  | Total power consumpation
150 Mins | [9 empty] | TN_2P |  |  |  |  | NA |  |  | 54 W * No. of link
180 Mins | [9 empty] | TN_6P |  |  |  |  | NA |  |  | 370 W * No. of link
210 Mins | [9 empty] | TN_20P |  |  |  |  | NA |  |  | 952 W * No. of link
240 Mins | [9 empty] | Ipasoo 200 NEC MW link |  |  |  |  | NA |  |  | 128 W * No. of link
[10 empty] | Ipasoo 400 NEC MW link |  |  |  |  | NA |  |  | 208 W * No. of link
[10 empty] | Ipasoo 1000 NEC MW link |  |  |  |  | NA |  |  | 453W * No. of link
[10 empty] | TN_6P//Mini link_6692 |  |  |  |  | 1 |  |  | NA
2.2 | Voltage Measured
String Number | Battery Number | Voltage Measured Before disconnecting Rectifier | 10 Mins |  | 30 Mins |  | 60 Mins |  | 90 Mins |  | 120 Mins |  | 150 Mins |  | 180 Mins |  | 210 Mins |  | 240 Mins
1 | 1 | 13.3 | 10.9
| 2 | 13.4 | 11
| 3 | 13.35 | 11
| 4 | 13.36 | 10.95
2 | 1 | 13.28 | 10.9
| 2 | 13.4 | 11.1
| 3 | 13.36 | 11
| 4 | 13.3 | 10.9
3 | 1
2
3
4
4 | 1
2
3
4
5 | 1
2
3
4
6 | 1
2
3
4